- STANDARD, LISTING AND APPROVAL

- NFPA 20

- UL (UL218)

- FM Global (Class 1321/1323)

- City of New York for fire pump service

- MANUFACTURER AND MODEL

- Tornatech model GPD

- SEISMIC CERTIFICATION

- Test Criteria

  - ICC-ES AC156

- Building Code

  - IBC 2015

  - CBC 2016

  - OSHPD Special Seismic Certification Preapproval – OSP

3.    Seismic Parameters

    - ASCE 7-10 Chapter 13

- ENCLOSURE

- NEMA 2

- Bottom conduit entry gland plate

- OPERATIONAL COMPONENTS

- Hand-OFF-Auto selector switch installed behind lockable breakable cover.

- TOUCH SCREEN OPERATOR INTERFACE

- 7.0” LCD color touch screen (HMI technology) operator interface powered by an embedded microcomputer with software PLC logic

- Keypad type pushbuttons:

  - Crank from Battery #1

  - Crank from Battery #2

  - Stop

  - Run test

- On-Screen Menu:

- Home

- Alarms

- Configuration

- History

- Service

- Manuals

- Language

- Shall graphically display:

  - AC power present

  - Charger #1 and #2 charging mode

  - Battery #1 and #2 voltage and amperage

  - System pressure

  - Cut-out and cut-in pressure settings

  - Starter #1 and #2 rest or cranking

  - Engine stopped / running

  - Type of starting cause

  - Fuel solenoid valve energized / not energized

  - Timers counting

  - Hand-OFF-Auto selector switch position

  - Actuation mode

  - Type of controller

  - Method of shutdown

  - Time and date

  - Pump room temperature       (⁰F or ⁰C)

  - Digital pressure gauge

- System pressure selectable units of measure:

  - PSI

  - kPa

  - Bar

  - Feet of head

  - Meter of water

- Shall allow programming and display of:

  - Cut-In and Cut-Out pressure settings

  - Minimum run period timer

  - Sequential start timer

  - Periodic test timer

- Shall allow selection of the language of operation.

- Shall allow on-screen viewing and downloading of the corresponding Operation Manual in the chosen language.

- COMMUNICATION PROTOCOL CAPABILITY

- Modbus with TCP/IP frame format and shielded female RJ45 connector

- STATE AND ALARM VISUAL INDICATORS

- Shall visually indicate and differentiate the criticalness by color:

- AC fail

- DC fail

- Battery fail 1, 2

- Charger fail 1, 2

- Engine trouble

- Pump room trouble

- Controller trouble

- Service required

- Weak battery 1

- Weak battery 2

- Loss of continuity with Contactor 1

- Loss of continuity with Contactor 2

- Weekly test Cut-In not reached

- Weekly test check solenoid valve

- Faulty pressure transducer

- Low raw water flow

- Engine fail when running

- Engine fail to start

- Engine overspeed

- Low ambient temperature

- Pump on demand

- Invalid Cut-In

- Overpressure

- Underpressure

- Battery 1 overvoltage

- Battery 2 overvoltage

- Water reservoir low

- Fuel tank Leak

- Low fuel level

- High fuel level

- Engine ECM in alternate position

- Engine fuel injection malfunction

- Engine high temperature

- Engine low temperature

- Engine ECM warning

- Engine ECM fault

- Engine low oil pressure

- High raw water temperature

- Low suction pressure

- Engine Run

- Main switch AUTO

- Pump room temperature (F or C)

- Periodic test

- Main switch in HAND

- Cranking cycle

- Main switch in OFF

- AC Power available

- CRANK CYCLE

- Crank from battery 1 for 15 seconds

- Rest for 15 seconds

- Crank from Battery 2 for 15 seconds

- Shall repeat 3 times. Visual alarm “Fail TO Start” shall appear if the engine does not start after the completion of this cycle.

- PRESSURE AND EVENT RECORDING

- Shall be capable of logging pressure data and operational events with time and date stamp.

- Shall be able to display operational events for the life of the controller, and display the pressure data in text and/or graphic form.

- Data shall be retrievable and downloadable to a USB drive or mobile app.

a.  All time statistics

      - First start up

      - On time

    - First and last service statistics

      - First setup

      - On time

      - Engine Statistics:

        - On time

        - Start count

        - Last start time

      - Minimum, maximum, average system pressure

      - Minimum, maximum, average pump room temperature

      - Jockey Pump controller

        - On time

        - Start count

        - Last start time

- PRESSURE SENSING - WETTED PARTS

- Shall be supplied with a pressure transducer (system) and run test solenoid valve assembly rated for 500psi working pressure (calibrated at 0-300psi) and be externally mounted with a protective cover

- Pressure sensing line connection to the pressure transducer shall be ½” FNPT

- Provision for a redundant pressure transducer shall be provided

- SERVICE/FLOW TESTING CAPABILITIES

- Shall have the capability of scheduling maintenance reminders

- Shall also have the capability of inputting pump flow test data, generate and display the pump curve and store this information in memory for the lifetime of the controller.

- CONNECTION FOR EXTERNAL DEVICES (devices and switches by others)

- Low fuel level switch

- Remote auto start device

- Water reservoir low switch

- Fuel tank leak switch

- High fuel level switch

- DPDT DRY CONTACTS FOR REMOTE INDICATION (8A – 250VAC):

- Engine run

- Main switch in HAND or OFF

- Common controller trouble (fail safe)

- Common engine trouble                    (field re-assignable)

- Common pump room alarm             (field re-assignable)

- Field programmable

- AUDIBLE ALARM

- Alarm buzzer - 85dB at 3 meters