- STANDARD, LISTING AND APPROVAL

  - NFPA 20

  - UL (UL218, UL1008)

  - FM Global (Approvals Class 1321/1323)

  - City of New York for fire pump service

- MANUFACTURER AND MODEL

  - Tornatech model GPP

- SEISMIC CERTIFICATION

  - Test criteria

    - ICC-ES AC156

  - Building Code

    - IBC 2015

    - CBC 2016

    - OSHPD Special Seismic Certification Preapproval – OSP

  - Seismic Parameters

    - ASCE 7-10 Chapter 13

- OPERATION AND STARTING METHOD

  - Full service combined manual and automatic

  - Reduced voltage part winding starting

- SHORT CIRCUIT WITHSTAND RATING

  - 200V - 480V = 100 kA / 600V = 50kA

- ENCLOSURE

  - NEMA 2

  - Bottom conduit entry gland plate

  - Lifting lugs

- POWER CIRCUIT COMPONENTS

  - Voltage surge arrestor

  - Isolating switch and circuit breaker assembly rated not less than 115% of the motor FLC.

  - Circuit breaker overcurrent sensing shall be non-thermal type, magnetic only.

  - Locked rotor protector to trip circuit breaker within 8 to 20 seconds at 600% of FLC.

  - Part winding starter

- OPERATIONAL COMPONENTS

  - Externally flange mounted common operating handles for both isolating switch and the circuit breaker assembly.

  - Mechanically interlocked with enclosure door to prohibit access in the "ON" position.

  - Emergency Start and run handle mechanism latchable in the “ON” position

- TOUCH SCREEN OPERATOR INTERFACE

  - 7.0” LCD color touch screen (HMI technology) powered by an embedded microcomputer with software PLC logic.

  - Keypad type pushbuttons:

    - Start

    - Stop

    - Run test

  - On-Screen Menu:

    - Home

    - Alarms

    - Configuration

    - History

    - Service

    - Manuals

    - Language

  - Shall graphically display:

    - Voltage and amperage readings of all three phases simultaneously and independently displayed with true RMS technology.

    - Motor starting transition

    - Motor stopped / running

    - Type of starting cause

    - Actuation mode

    - Type of controller

    - Method of shutdown

    - Time and date

    - Pump room temperature (⁰F or ⁰C)

    - Digital pressure gauge

  - System pressure selectable units of measure:

    - PSI

    - kPA

    - Bar

    - Feet of head

    - Meter of water

  - Shall allow programming and display of:

    - Cut-In and Cut-Out pressure settings

    - Minimum run period timer

    - Sequential start timer

    - Periodic test timer

  - Shall allow selection of the language of operation.

  - Shall allow on-screen viewing and downloading of the corresponding Operation Manual in the chosen language.

- COMMUNICATION PROTOCOL CAPABILITY

  - Modbus with TCP/IP frame format and shielded female RJ45 connector

- STATE AND ALARM VISUAL INDICATORS

  - Shall visually indicate and differentiate the criticalness by color:

    - Locked rotor current

    - Fail to start

    - Under current

    - Over current

    - Under voltage

    - Over voltage

    - Phase unbalance

    - Check weekly test solenoid valve

    - Weekly test cut-in not reached

    - Transducer fault

    - Control voltage not healthy

    - Motor trouble

    - Pump room alarm

    - Invalid cut-in

    - Phase reversal

    - Power loss

    - Phase Loss L1

    - Phase Loss L2

    - Phase Loss L3

    - Low water level

    - Pump on demand

    - Low ambient temp

    - Service required

- PRESSURE AND EVENT RECORDING

  - Shall be capable of logging pressure data and operational events with time and date stamp.

  - Shall be able to display operational events for the life of the controller, and display the pressure data in text and/or graphic form.

  - Data shall be retrievable and downloadable to a flash memory disk via the USB port accessible to the user without having to open the controller door.

    - All time statistics

      - First start up

      - On time

    - First and last service statistics

      - First setup

      - On time

      - Motor Statistics:

        - On time

        - Start count

        - Last start time

      - Minimum, maximum, average system pressure

      - Minimum, maximum, average pump room temperature

      - Jockey Pump controller

        - On time

        - Start count

        - Last start time

    - Power statistics

      - Voltage between phases with date stamp

      - Amperage per phase with date stamp

- WETTED PARTS

  - Shall be supplied with a pressure transducer and run test solenoid valve assembly rated for 500psi working pressure (calibrated at 0-300psi) and be externally mounted with a protective cover.

  - Pressure sensing line connection to shall be ½” FNPT.

  - Provision for a redundant pressure transducer shall be provided.

- SERVICE/FLOW TESTING CAPABILITIES

  - Shall have capability of scheduling maintenance reminders.

  - Shall have capability of inputting pump flow test data, generate and display the pump curve and store this information in memory for the lifetime of the controller.

- CONNECTION FOR EXTERNAL DEVICES

  - Manual remote start device

  - Automatic remote start device

  - Deluge valve start

- DPDT DRY CONTACTS FOR REMOTE INDICATION OF ALARM CONDITIONS (8A – 250VAC)

  - Power or phase failure and/or circuit breaker in open position

  - Phase reversal

  - Pump run

  - Common pump room alarm (field re-assignable)

  - Common motor trouble (field re-assignable)

  - Field programmable

- AUDIBLE ALARM

  - 6” alarm bell rated for 85dB at 10ft (3m)