**UL Listed Disconnecting Means**

The UL Listed disconnecting means shall be a model OPD as manufactured by Tornatech, rated for \_\_\_\_\_\_\_V. / \_\_\_\_\_\_ HP / \_\_\_\_\_ phase / \_\_\_\_\_ Hz and specifically designed to assure complete upstream overcurrent protection coordination with the electric fire pump controller. It shall have the following features:

* Factory assembled, wired, and tested
* UL Listed for fire pump service as per NFPA70 (NEC) 695.4(B)(2)(a)(2) and 695.3(F)(2)
* Suitable as service entrance equipment
* NEMA 2 assembly
* Flange mounted disconnect handle lockable in the ON (closed position)
* Markings as per NFPA70 (NEC) 695.4(B)(3)(a)(2)